4-Point Inspection Form

Insured/Applicant Name:	 Mr. ABC 	        Application / Policy #:	 6293CGg267

Address Inspected:	1345 Marseille Dr, Miami Beach FL 33141

Actual Year Built:     1949	Date Inspected:	12/20/2021

Minimum Photo Requirements

Dwelling: Each side   Roof: Each slope  Plumbing: Water heater, under cabinet plumbing/drains, exposed valves  Main electrical service panel with interior door label

Electrical box with panel off

All hazards or deficiencies noted in this report

A Florida-licensed inspector must complete, sign and date this form.

Be advised that Underwriting will rely on the information in this sample form, or a similar form, that is obtained from the Florida licensed professional of your choice. This information only is used to determine insurability and is not a warranty or assurance of the suitability, fitness or longevity of any of the systems inspected.

| Electrical System Separate documentation of any aluminum wiring remediation must be provided and certified by a licensed electrician. |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Main Panel Type: Circuit breaker Fuse Total Amps: 125 |  |  |  | Second Panel Type: Circuit breaker Fuse Total Amps: 125 |  |  |  |
| Is amperage sufficient for current usage? | Yes | No (explain) |  | Is amperage sufficient for current usage? |  | Yes | No (explain) |
| Indicate presence of any of the following: Cloth wiring Active knob and tube Branch circuit aluminum wiring (If present, describe the usage of all aluminum wiring): * If single strand (aluminum branch) wiring, provide details of all remediation. Separate documentation of all work must be provided. Connections repair via COPALUM crimp Connections repair via AlumniConn |  |  |  |  |  |  |  |
| Hazards Present |  |  |  |  |  |  |  |
| Blowing fuses Tripping breakers Empty sockets Loose Wiring Improper grounding Corrosion Over fusing |  |  |  | Double taps Exposed wiring Unsafe wiring Improper breaker size Scorching Other (explain) |  |  |  |
| General condition of the electrical system: Satisfactory Unsatisfactory (explain) Double tapped breaker was noted in the secondary electric panel breaker number nine. |  |  |  |  |  |  |  |
| Supplemental information |  |  |  |  |  |  |  |
| Main Panel |  |  | Second Panel |  | Wiring Type Copper NM, BX or Conduit |  |  |
| Panel age: |  |  | Panel age: |  |  |  |  |
| Year last updated: |  |  | Year last updated: |  |  |  |  |
| Brand/Model: General Electric |  |  | Brand/Model: General Electric |  |  |  |  |

A1 Florida Home Inspections 12/20/2021

4-Point Inspection Form

HVAC System

Central AC: Yes No Central heat: Yes No If not central heat, indicate primary heat source and fuel type: Are the heating, ventilation and air conditioning systems in good working order? Yes No (explain) Date of last HVAC servicing/inspection:

Hazards Present Wood burning stove or central gas fireplacenotprofessionally installed? Yes No Space heater used as primary heat source? Yes No Is the source portable? Yes No Does the air handler/condensate line or drain pan show any signs of blockage or leakage, including water damage to the surrounding area? Yes No

Supplemental Information

Age of system: 5 Year last updated: 2016 (Please attach photo(s) of HVAC equipment, including dated manufacturer’s plate)

| Plumbing System |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Is there a temperature pressure relief valve on the water heater? Is there any indication of an active leak? Yes No Is there any indication of a prior leak? Yes No Water heater location: Exterior utility closet | Yes | No |  |  |  |  |
| General condition of the following plumbing fixtures and connections to applicances: |  |  |  |  |  |  |
| Satisfactory Unsatisfactory | N/A |  | Toilets Sinks Sump pump Main shut off valve All other visible | Satisfactory | Unsatisfactory | N/A |
| Dishwasher |  |  |  |  |  |  |
| Refrigerator |  |  |  |  |  |  |
| Washing Machine |  |  |  |  |  |  |
| Water Heater |  |  |  |  |  |  |
| Showers/Tubs |  |  |  |  |  |  |
| If unsatisfactory, please provide comments/details (leaks, wet/soft spots, mold, corrosion, grout/caulk, etc.). |  |  |  |  |  |  |
| Supplemental Information |  |  |  |  |  |  |
| Age of Piping System: X Original to home Completely re-piped Partially re-piped (Provide year and extent of renovation in the comments below) |  |  | T ype of pipes (check all that apply) |  |  |  |
|  |  |  | Copper |  |  |  |
|  |  |  | PVC/CPVC |  |  |  |
|  |  |  | Galvanized |  |  |  |
|  |  |  | PEX |  |  |  |
|  |  |  | Polybutylene |  |  |  |
|  |  |  | Other (specify) |  |  |  |

A1 Florida Home Inspections 12/20/2021

4-Point Inspection Form

| Roof (With photos of each roof slope, this section can take the place of the Roof Inspection Form.) |  |
| --- | --- |
| Predominant Roof Covering material: Modified Bitumen Roof age (years): 25 Remaining useful life (years): 5 Date of last roofing permit: 07/03/1996 Date of last update: 07/03/1996 If updated (check one): Full Replacement Partial Replacement % of replacement Overall condition: Satisfactory Unsatisfactory (explain below) Any visible signs of damage / deterioration? (check all that apply and explain below) Cracking Cupping/Curling Excessive granule loss Exposed asphalt Exposed felt Missing/loose/cracked tabs or tiles Soft spots in decking Visible hail damage Any visible signs of leaks Yes No Attic/underside of decking Yes No Interior ceilings Yes No | Secondary Roof Covering material: 3-Tab Roof age (years): 25 Remaining useful life (years): 5 Date of last roofing permit: 07/03/1996 Date of last update: If updated (check one): Full Replacement Partial Replacement % of replacement Overall condition: Satisfactory Unsatisfactory (explain below) Any visible signs of damage / deterioration? (check all that apply and explain below) Cracking Cupping/Curling Excessive granule loss Exposed asphalt Exposed felt Missing/loose/cracked tabs or tiles Soft spots in decking Visible hail damage Any visible signs of leaks Yes No Attic/underside of decking Yes No Interior ceilings Yes No |

305-898-6123

Work Phone

Home Inspector

License Type

A1 Florida Home Inspections

Company Name

12/29/2021

Date

HI10320

License Number

InterNachi CPI

Title

Inspector Signature

All 4-Point Inspection Formsmust be completed and signed by a verifiable Florida-licensed inspector.

I certify that the above statements are true and correct.

Additional Comments/Observations(use additional pages if needed):

A1 Florida Home Inspections 12/20/2021

4-Point Inspection Form

Photos must accompany each4-Point Inspection Form.The minimum photo requirements include: Dwelling: Each side

Roof: Each slope

Plumbing: Water heater, under cabinet plumbing/drains, exposed valves Open main electrical panel and interior door

Electrical box with the panel off

Allhazards or deficiencies

Photo Requirements

To be accepted, all inspection forms must be completed, signed and dated by a verifiable Florida-licensed professional.Examplesinclude: A general, residential, or building contractor

A building code inspector A home inspector

Note:A trade-specific, licensed professional may sign off only on the inspection form section for their trade. (e.g., an electrician may sign off only on the electrical section of the form.)

Inspector Requirements

The Florida-licensed inspector is required to certify the condition of the roof, electrical, HVAC and plumbing systems.Acceptable Conditionmeans that each system is working as intended and there are no visible hazards or deficiencies.

Documenting the Condition of Each System

This section of the4-Point Inspection Formmust be completed with full details/descriptions if any of the following are noted on the inspection: Updates: Identify the types of updates, dates completed and by whom

Any visible hazards or deficiencies

Any system determined not to be in good working order

Additional Comments or Observations

The writing agent must review each 4-Point Inspection Form before it is submitted with an application for coverage. It is the agent’s responsibility to ensure that all rules and requirements are met before the application is bound. Agents may not submit applications for properties with electrical, heating or plumbing systems not in good working order or with existing hazards/deficiencies.

Note to All Agents

Special Instructions:This sample4-Point Inspection Formincludes the minimum data needed for Underwriting to properly evaluate a property application. While this specific form is not required, any other inspection report submitted for consideration must include at least this level of detail to be acceptable.

Exterior Photos

Photos, Additional Comments or Observations

North	West	West

South	East

Electrical System

Panel Photos

Additional Photos

Hazards

Double tap the breaker and secondary electric panel

HVAC System

HVAC Equipment

Plumbing System

Water Heater

Demand water heater

Under cabinet plumbing & drains

Exposed Valves

Roof

Photos of Each Slope

(

. kJL ..

- * . fi T

••	• 	iv

Ik	;.a'V"

*

»»

PPH.

  - *4